{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["OUTPUT","Table_A-1_Data_Pos_Up","Table_A-1_Data_Pos_Down","Table_A-1_Data_Neg_Up","Table_A-1_Data_Neg_Down"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"OUTPUT","index":0,"n_rows":5,"n_cols":20,"rows_kept":5,"cut":false,"hidden":false,"merged":[[1,2,1,5],[1,0,1,1],[2,1,4,1],[0,0,0,19],[2,0,4,0],[2,4,4,4],[2,2,3,3],[2,13,4,13],[1,13,1,19],[2,18,4,18],[2,17,4,17],[2,19,4,19],[3,7,3,8],[2,5,2,8],[3,15,3,16],[2,14,2,16],[3,5,3,6]]}
[]
["Project:",null,null,null,null,null,"Rep:",null,"Engr.:"]
["Item","TAG (Location)","Duct Size (in)",null,"Pressure","Immediate Up/Downstream Disturbances",null,null,null,null,null,null,null,"Z","Locate Probes",null,null,"Source","Inst. ACC ±","Diagram"]
[null,null,null,null,null,"Upstream",null,"Downstream",null,null,null,null,null,null,"Opt.","Range"]
[null,null,"Width","Height",null,"Description","Fig.","Description","Fig.","Xmin","Xcalc","Ymin","Ycalc",null,"L","X","Y"]

{"sheet":"Table_A-1_Data_Pos_Up","index":1,"n_rows":24,"n_cols":4,"rows_kept":24,"cut":false,"hidden":true,"merged":[[0,1,0,3],[1,1,1,3],[2,1,3,1],[2,2,2,3],[4,1,4,3]]}
["RELATIONSHIP TO FAN →","POSITIVE"]
[null,"Upstream"]
[null,"Figure","X"]
[null,null,"Xmin","Xcalc"]
["Disturbance  ↓"]
["Air Cleaners - Filter (pleated)","A-X-01",24]
["Air Cleaners - Filter (roll)","A-X-02",12]
["Coils and Heaters - H/W Coil","C-X-01",18]
["Coils and Heaters - C/W Coil","C-X-01",18]
["Dampers - Ducted (2-position, Open/Closed)","D-X-01",20]
["Elbow (no turning vanes)","E-X-01",36,3]
["Elbow (turning vanes)","E-X-02",9,0.75]
["Elbow (radius or sweep)","E-X-03",21,1.75]
["Fans (Ducted) - Centrifugal","F-X-01",24,2]
["Fans (Ducted) - Vane Axial","F-X-02",24,2]
["Fan Plenums - Plenum to Duct","P-X-01",18,1.5]
["T Main Duct (no turning vanes)","T-X-01",12,1]
["T Main Duct (turning vanes)","T-X-03",18,1.5]
["T Branch Duct (no turning vanes)","T-X-05",36,3]
["T Branch Duct (turning vanes)","T-X-06",18,1.5]
["Terminal T (no turning vanes)","T-X-07",36,3]
["Terminal T (turning vanes)","T-X-08",18,1.5]
["Reducing Transition","Z-X-01",6,0.5]
["Expanding Transition","Z-X-02",18,1.5]

{"sheet":"Table_A-1_Data_Pos_Down","index":2,"n_rows":22,"n_cols":4,"rows_kept":22,"cut":false,"hidden":true,"merged":[[0,1,0,3],[1,1,1,3],[2,1,3,1],[2,2,2,3],[4,1,4,3]]}
["RELATIONSHIP TO FAN →","POSITIVE"]
[null,"Downstream"]
[null,"Figure","Y"]
[null,null,"Ymin","Ycalc"]
["Disturbance  ↓"]
["Air Cleaners - Filter (pleated)","A-Y-01",6]
["Air Cleaners - Filter (roll)","A-Y-02",6]
["Coils and Heaters - H/W Coil","C-Y-01",6]
["Coils and Heaters - C/W Coil","C-Y-01",6]
["Dampers - Ducted (Modulating)","D-Y-01",9,0.75]
["Dampers - Ducted (2-position, Open/Closed)","D-Y-01",10]
["Elbow (no turning vanes)","E-Y-01",18,1.5]
["Elbow (turning vanes)","E-Y-02",9,0.75]
["Elbow (radius or sweep)","E-Y-03",21,1.75]
["Exhaust Louvers - Backdraft","L-Y-01",30]
["Exhaust Louvers - Stationary","L-Y-01",18]
["T Main Duct (no turning vanes)","T-Y-01",6,0.5]
["T Main Duct (turning vanes)","T-Y-03",6,0.5]
["Terminal T (no turning vanes)","T-Y-07",12,1]
["Terminal T (turning vanes)","T-Y-08",9,0.75]
["Reducing Transition","Z-Y-01",6,0.5]
["Expanding Transition","Z-Y-02",6,0.5]

{"sheet":"Table_A-1_Data_Neg_Up","index":3,"n_rows":33,"n_cols":4,"rows_kept":33,"cut":false,"hidden":true,"merged":[[0,1,0,3],[1,1,1,3],[2,1,3,1],[2,2,2,3],[4,1,4,3]]}
["RELATIONSHIP TO FAN →","NEGATIVE"]
[null,"Upstream"]
[null,"Figure","X"]
[null,null,"Xmin","Xcalc"]
["Disturbance  ↓"]
["Air Cleaners - Filter (pleated)","A-X-01",18]
["Air Cleaners - Filter (roll)","A-X-02",12]
["Coils and Heaters - H/W Coil","C-X-01",18]
["Coils and Heaters - C/W Coil","C-X-01",18]
["Dampers - Ducted (2-position, Open/Closed)","D-X-01",20]
["Elbow (no turning vanes)","E-X-01",36,3]
["Elbow (turning vanes)","E-X-02",9,0.75]
["Elbow (radius or sweep)","E-X-03",21,1.75]
["OA Intake - Angled (or Radiused) Hoods","H-X-01",12]
["OA Intake - Straight Through Hoods","H-X-02",12]
["OA Intake - Hurricane/Rain Louvers <500 FPM","L-X-01",18]
["OA Intake - Hurricane/Rain Louvers 500 to 1,250 FPM","L-X-01",24]
["OA Intake - Hurricane/Rain Louvers >1,250 FPM","L-X-01",36]
["OA Intake - Stationary Louvers < 6 in. <500 FPM","L-X-01",18]
["OA Intake - Stationary Louvers < 6 in. 500 to 1,250 FPM","L-X-01",24]
["OA Intake - Stationary Louvers < 6 in. >1,250 FPM","L-X-01",36]
["OA Intake - Stationary Louvers ≥ 6 in. <500 FPM","L-X-01",12]
["OA Intake - Stationary Louvers ≥ 6 in. 500 to 1,250 FPM","L-X-01",18]
["OA Intake - Stationary Louvers ≥ 6 in. >1,250 FPM","L-X-01",24]
["Outdoor Air Intake Plenum to Duct <500 FPM","P-X-01",6]
["Outdoor Air Intake Plenum to Duct 500 to 1,250 FPM","P-X-01",12]
["Outdoor Air Intake Plenum to Duct >1,250 FPM","P-X-01",18]
["T Main Duct (no turning vanes)","T-X-02",18,1.5]
["T Main Duct (turning vanes)","T-X-04",12,1]
["Terminal T (no turning vanes)","T-X-07",24,2]
["Terminal T (turning vanes)","T-X-08",12,1]
["Reducing Transition","Z-X-01",6,0.5]
["Expanding Transition","Z-X-02",18,1.5]

{"sheet":"Table_A-1_Data_Neg_Down","index":4,"n_rows":28,"n_cols":4,"rows_kept":28,"cut":false,"hidden":true,"merged":[[0,1,0,3],[1,1,1,3],[2,1,3,1],[2,2,2,3],[4,1,4,3]]}
["RELATIONSHIP TO FAN →","NEGATIVE"]
[null,"Downstream"]
[null,"Figure","Y"]
[null,null,"Ymin","Ycalc"]
["Disturbance  ↓"]
["Air Cleaners - Filter (pleated)","A-Y-01",6]
["Air Cleaners - Filter (roll)","A-Y-02",6]
["Coils and Heaters - H/W Coil","C-Y-01",6]
["Coils and Heaters - C/W Coil","C-Y-01",6]
["Dampers - Ducted (Modulating)","D-Y-01",9,0.75]
["Dampers - Ducted (2-position, Open/Closed)","D-Y-01",10]
["Dampers - OA Intake 4 in. Blade ≤1,250 FPM","D-Y-01",4]
["Dampers - OA Intake 6 in. Blade ≤1,250 FPM","D-Y-01",6]
["Dampers - OA Intake 8 in. Blade ≤1,250 FPM","D-Y-01",8]
["Elbow (no turning vanes)","E-Y-01",18,1.5]
["Elbow (turning vanes)","E-Y-02",9,0.75]
["Elbow (radius or sweep)","E-Y-03",21,1.75]
["Fans (Ducted) - Centrifugal","F-Y-01",12,1]
["Fans (Ducted) - Vane Axial","F-Y-02",12,1]
["Fan Plenums - Duct to Plenum","P-Y-01",12,1]
["T Main Duct (no turning vanes)","T-Y-02",6,0.5]
["T Main Duct (turning vanes)","T-Y-04",6,0.5]
["T Branch Duct (no turning vanes)","T-Y-05",12,1]
["T Branch Duct (turning vanes)","T-Y-06",12,1]
["Terminal T (no turning vanes)","T-Y-07",6,0.5]
["Terminal T (turning vanes)","T-Y-08",6,0.5]
["Reducing Transition","Z-Y-01",6,0.5]
["Expanding Transition","Z-Y-02",6,0.5]